{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["Sheet1","Sheet3"],"not_rendered":{"charts":0,"images":2,"macros":1,"external_links":0,"defined_names":5,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":39,"n_cols":77,"rows_kept":39,"cut":false,"hidden":false,"merged":[[19,1,19,9],[19,11,19,19],[9,1,9,9],[9,11,9,19],[1,1,1,4],[2,1,2,4],[3,1,3,4],[0,56,0,64],[0,65,0,72],[6,1,7,1],[6,8,7,8],[0,29,0,37],[0,38,0,45]]}
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Instructions:",null,null,null,"Updated","2015-06-19",null,null,null,null,null,null,null,null,null,"Inlet",null,null,null,null,null,null,null,null,"Discharge",null,null,null,null,null,null,null,null,null,null,{"$f":"$E$7*VLOOKUP($C$7,DECIDER,2,FALSE)/$E$9","v":9774.8506039415133},{"$f":"$E$8*(VLOOKUP($C$7,DECIDER,2,FALSE)/$E$9)^2","v":2.0992222133758283},null,{"$f":"BB1*BC1","v":1},{"$f":"$E$7*VLOOKUP($C$7,DECIDER,2,FALSE)/$E$9>VLOOKUP($C$7,DECIDER,3,FALSE)","v":true},{"$f":"$E$8*(VLOOKUP($C$7,DECIDER,2,FALSE)/$E$9)^2<VLOOKUP($C$7,DECIDER,4,FALSE)","v":true},null,"Inlet",null,null,null,null,null,null,null,null,"Discharge"]
["Quote/Project#:",3268,null,null,null,null,null,null,null,null,null,null,null,null,"1. Enter project information in \"green\" cells.",null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,null,null,{"$f":"$L$7*VLOOKUP($J$7,DECIDER,2,FALSE)/$L$9","v":{"$error":"#N/A"}},{"$f":"$L$8*(VLOOKUP($J$7,DECIDER,2,FALSE)/$L$9)^2","v":{"$error":"#N/A"}},null,{"$f":"BB2*BC2","v":{"$error":"#N/A"}},{"$f":"$L$7*VLOOKUP($J$7,DECIDER,2,FALSE)/$L$9>VLOOKUP($J$7,DECIDER,3,FALSE)","v":{"$error":"#N/A"}},{"$f":"$L$8*(VLOOKUP($J$7,DECIDER,2,FALSE)/$L$9)^2<VLOOKUP($J$7,DECIDER,4,FALSE)","v":{"$error":"#N/A"}},1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19]
["Customer/JOB:","Georgetown Behavioral",null,null,null,null,null,null,null,null,null,null,null,null,"2. Enter Supply and Exhaust (if selected) blower information.",null,null,null,null,null,null,null,null,null,null,null,null,null,null,63,125,250,500,1000,2000,4000,8000,"Tot.",63,125,250,500,1000,2000,4000,8000,"Tot.","CFM","\" w.g.","RPM","MAX RPM","Decider","RPM","CFM","\"wg",null,63,125,250,500,1000,2000,4000,8000,"Tot.",63,125,250,500,1000,2000,4000,8000,"Tot.","CFM","\" w.g.","RPM"]
["Addison Rep:","-",null,null,null,null,null,null,null,null,null,null,null,null,"3. Add to schedule below.",null,null,null,null,null,null,null,null,null,null,null,null,null,"10\" BI",93,92,91,88,76,70,71,66,98,83,90,96,97,86,77,78,71,100,811,6.1,3900,5200,"10\" BI",5200,1434,9.75,"10\" BI",85,81,80,81,76,70,71,66,88,75,78,84,88,86,77,76,68,92,1413,3.9,3900]
[null,null,null,null,null,null,null,"Check if EXHAUST FAN available",null,null,null,null,null,null,"4. Repeat steps 2-3 for multiple units.",null,null,null,null,null,null,null,null,null,null,null,null,null,"11\" BI",97,94,91,88,78,73,72,68,99,86,91,95,96,87,79,78,72,100,638,5,3231,4735,"11\" BI",2659,928,3.08,"11\" BI",88,83,82,85,78,73,73,73,91,77,79,85,91,87,79,77,74,94,1948,4,3700]
[null,"Unit#","PRRA480 RTU-3",null,null,null,null,null,null,null,null,null,null,null,"5. Reset schedule to clear.",null,null,null,null,null,null,null,null,null,null,null,null,null,"12\" BI",91,87,87,86,74,70,68,65,94,82,86,93,96,85,78,76,71,98,1200,5,2873,4315,"12\" BI",2234,1294,2.72,"12\" BI",87,79,80,82,77,74,72,69,90,79,78,86,91,89,83,79,73,95,2485,4.5,3300]
[null,"Supply Fan","25\" AF","CFM",12440,null,null,null,"Exhaust Fan",null,"CFM",0,null,null,"6. Select cells to delete single record.",null,null,null,null,null,null,null,null,null,null,null,null,null,"14\" BI",96,96,94,81,76,76,74,69,101,86,94,99,90,86,83,81,74,101,1300,5,2509,3825,"14\" BI",1940,1677,2.75,"14\" BI",85,80,81,80,76,75,73,73,89,76,78,86,88,87,83,79,76,93,2985,4,2700]
[null,null,null,"TSP",3.4,null,null,null,null,null,"TSP",0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16\" BI",95,95,94,82,77,77,72,67,99,83,91,98,89,86,81,74,70,100,2526,6,2400,3400,"16\" BI",3134,3600,8.5,"16\" BI",93,85,85,86,81,79,78,76,95,84,84,90,95,91,84,81,79,98,4200,6,2944]
[null,null,null,"RPM",1573,null,null,null,null,null,"RPM",0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18\" BI",89,87,94,82,75,76,76,71,97,79,85,100,91,86,82,80,76,101,3000,6,2220,3025,"18\" BI",3000,5200,10,"18\" BI",88,83,86,86,81,82,81,76,93,81,84,93,97,93,89,86,81,100,6000,6,2718]
["Sound Data","RETURN",null,null,null,null,null,null,null,null,null,"DISCHARGE",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20\" BI",90,91,92,82,79,78,77,72,97,83,91,100,93,89,84,84,79,102,3000,5,1821,2720,"20\" BI",2347,5631,7.26,"20\" BI",91,85,91,86,84,84,85,82,96,87,84,98,96,92,90,91,86,102,8005,4.5,2400]
[null,63,125,250,500,1000,2000,4000,8000," dBA",null,63,125,250,500,1000,2000,4000,8000,"dBA",null,null,null,null,null,null,null,null,"22\" BI",91,92,95,82,81,80,80,74,98,82,90,101,91,89,84,85,79,103,4000,5,1631,2430,"22\" BI",1734,5889,5.09,"22\" BI",91,89,91,86,85,84,86,80,97,88,89,99,97,94,91,93,85,103,10205,4.5,2100]
[{"$f":"C6","v":"PRRA480 RTU-3"},{"$f":"AD35+B13","v":59.716962825222538},{"$f":"AE35+C13","v":62.716962825222538},{"$f":"AF35+D13","v":73.716962825222538},72.716962825222538,73.716962825222538,69.716962825222538,69.716962825222538,65.716962825222538,{"$f":"10*LOG((10^(B12/10)+10^(C12/10)+10^(D12/10)+10^(E12/10)+10^(F12/10)+10^(G12/10)+10^(H12/10)+10^(I12/10)))","v":79.592136724173557},null,{"$f":"AM35+L13","v":64.716962825222538},{"$f":"AN35+M13","v":69.716962825222538},82.716962825222538,85.716962825222538,86.716962825222538,81.716962825222538,78.716962825222538,72.716962825222538,{"$f":"10*LOG((10^(L12/10)+10^(M12/10)+10^(N12/10)+10^(O12/10)+10^(P12/10)+10^(Q12/10)+10^(R12/10)+10^(S12/10)))","v":91.083717311778003},null,null,null,null,null,null,null,null,"25\" BI",95,100,88,80,79,77,76,71,102,89,101,97,92,90,84,84,79,103,5000,5,1437,2150,"25\" BI",1354,6187,4.16,"25\" BI",95,90,92,85,86,83,85,82,99,93,91,101,97,96,91,93,88,104,13000,3.5,1800]
[null,-26,-16,-9,-3,0,1,1,-1,null,null,-26,-16,-9,-3,0,1,1,-1,null,null,null,null,null,null,null,null,null,"12\" AF",85,80,77,82,76,76,69,66,89,79,79,79,88,85,85,79,78,92,3000,5,3334,4500,"12\" AF",3340,3554,3.55,"12\" AF",95,89,84,88,83,82,79,78,97,92,88,87,96,93,91,86,87,100,4379,3.31,3793]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14\" AF",88,80,78,82,75,73,67,64,90,94,86,84,88,81,79,73,70,96,2600,5,2670,4000,"14\" AF",3074,4884,2.87,"14\" AF",88,80,78,82,75,73,67,64,90,94,86,84,88,81,79,73,70,96,2600,5,2670]
[{"$f":"A2","v":"Quote/Project#:"},3268,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16\" AF",87,82,81,84,77,73,68,66,91,85,80,81,87,84,81,77,75,92,2600,5,2520,3700,"16\" AF",3416,6909,6.16,"16\" AF",100,94,90,93,88,87,83,85,102,97,90,90,98,95,93,88,86,103,7500,4.16,3385]
["Customer/JOB:","Georgetown Behavioral",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18\" AF",75,73,77,74,74,70,67,61,83,83,79,87,85,84,79,74,70,91,4379,3.31,1816,3300,"18\" AF",2582,7909,4.13,"18\" AF",90,87,88,89,84,82,83,78,95,95,91,94,99,97,93,89,82,103,8500,3,2585]
["Addison Rep:","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20\" AF",77,73,83,71,74,69,67,60,85,83,78,88,84,84,79,76,72,91,5500,3,1624,2850,"20\" AF",2032,8363,3.17,"20\" AF",92,87,87,88,83,83,85,79,96,94,90,92,96,95,91,89,84,102,10000,3,2278]
[null,null,null,null,null,null,null,{"$f":"IF(T1-TODAY()>93,\"**THIS TOOL MAY HAVE BEEN RELPLACED BY A NEWER VERSION. CHECK FOR UPDATES AT WWW.ADDISON-HVAC.COM\",\"\")","v":""},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22\" AF",80,74,83,71,70,67,63,59,86,82,75,84,81,80,75,71,68,89,5500,3,1340,2650,"22\" AF",1577,7627,3.6,"22\" AF",88,82,87,79,78,76,71,68,92,90,87,94,91,90,85,80,76,98,10000,3,1733]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"25\" AF",82,77,83,73,71,66,67,64,86,85,78,86,82,80,77,73,70,90,7500,3,1220,2350,"25\" AF",1236,9338,2.6,"25\" AF",89,82,86,79,77,72,72,70,92,91,86,92,89,87,81,78,74,97,12000,2,1388]
["Sound Data","RETURN",null,null,null,null,null,null,null,null,null,"DISCHARGE",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Dual 14\" BI",{"$f":"10*LOG(10^(AD7/10)+10^(AD7/10))","v":99.010299956639813},{"$f":"10*LOG(10^(AE7/10)+10^(AE7/10))","v":99.010299956639813},97.010299956639813,84.010299956639813,79.010299956639813,79.010299956639813,77.010299956639827,72.010299956639813,104.01029995663983,89.010299956639813,97.010299956639813,102.01029995663981,93.010299956639813,89.010299956639813,86.010299956639813,84.010299956639813,77.010299956639827,104.01029995663983,1300,5,2509,3825,"Dual 14\" ",1940,1677,2.75,"Dual 14\" ",{"$f":"10*LOG(10^(BE7/10)+10^(BE7/10))","v":88.010299956639813},83.010299956639813,84.010299956639813,83.010299956639813,79.010299956639813,78.010299956639827,76.010299956639813,76.010299956639813,92.010299956639841,79.010299956639813,81.010299956639813,89.010299956639813,91.010299956639841,90.010299956639813,86.010299956639813,82.010299956639813,{"$f":"10*LOG(10^(BU7/10)+10^(BU7/10))","v":79.010299956639813},96.010299956639813,2985,4,2700]
["Freq. Band",63,125,250,500,1000,2000,4000,8000,"Tot. dBA",null,63,125,250,500,1000,2000,4000,8000,"Tot. dBA",null,null,null,null,null,null,null,null,"Dual 16\" BI",{"$f":"10*LOG(10^(AD8/10)+10^(AD8/10))","v":98.010299956639813},98.010299956639813,97.010299956639813,85.010299956639813,80.010299956639827,80.010299956639827,75.010299956639827,70.010299956639827,102.01029995663981,86.010299956639813,94.010299956639827,101.01029995663981,92.010299956639841,89.010299956639813,84.010299956639813,77.010299956639827,73.010299956639813,103.01029995663981,2526,6,2400,3400,"Dual 16\" ",3134,3600,8.5,"Dual 16\" ",96.010299956639813,88.010299956639813,88.010299956639813,89.010299956639813,84.010299956639813,82.010299956639813,81.010299956639813,79.010299956639813,98.010299956639813,87.010299956639813,87.010299956639813,93.010299956639813,98.010299956639813,94.010299956639827,87.010299956639813,84.010299956639813,82.010299956639813,101.01029995663981,4200,6,2944]
["PRRA480 RTU-5",51.988578829361799,56.988578829361799,69.988578829361799,65.988578829361799,66.988578829361799,62.988578829361799,63.988578829361799,58.988578829361799,73.959997518728258,null,57.988578829361799,60.988578829361799,75.988578829361799,77.988578829361799,78.988578829361799,76.988578829361799,72.988578829361799,67.988578829361799,84.148490886344092,null,null,null,null,null,null,null,null,"Dual 18\" BI",92.010299956639841,90.010299956639813,97.010299956639813,85.010299956639813,78.010299956639827,79.010299956639813,79.010299956639813,74.010299956639813,100.01029995663981,82.010299956639813,88.010299956639813,103.01029995663981,94.010299956639827,89.010299956639813,85.010299956639813,83.010299956639813,79.010299956639813,104.01029995663983,3000,6,2220,3025,"Dual 18\" ",3000,5200,10,"Dual 18\" ",91.010299956639841,86.010299956639813,89.010299956639813,89.010299956639813,84.010299956639813,85.010299956639813,84.010299956639813,79.010299956639813,96.010299956639813,84.010299956639813,87.010299956639813,96.010299956639813,100.01029995663981,96.010299956639813,92.010299956639841,89.010299956639813,84.010299956639813,103.01029995663981,6000,6,2718]
["PRRA660 RTU-4",55.205628740853825,61.205628740853811,78.205628740853811,72.205628740853811,78.205628740853825,74.205628740853811,72.205628740853825,63.205628740853811,82.914247333109742,null,64.205628740853811,69.205628740853811,86.20562874085384,88.205628740853811,91.205628740853811,87.205628740853811,84.205628740853811,78.205628740853825,95.138698656679438,null,null,null,null,null,null,null,null,"Dual 20\" BI",93.010299956639813,94.010299956639827,95.010299956639827,85.010299956639813,82.010299956639813,81.010299956639813,80.010299956639827,75.010299956639827,100.01029995663981,86.010299956639813,94.010299956639827,103.01029995663981,96.010299956639813,92.010299956639841,87.010299956639813,87.010299956639813,82.010299956639813,105.01029995663983,3000,5,1821,2720,"Dual 20\" ",2347,5631,7.26,"Dual 20\" ",94.010299956639827,88.010299956639813,94.010299956639827,89.010299956639813,87.010299956639813,87.010299956639813,88.010299956639813,85.010299956639813,99.010299956639813,90.010299956639813,87.010299956639813,101.01029995663981,99.010299956639813,95.010299956639827,93.010299956639813,94.010299956639827,89.010299956639813,105.01029995663983,8005,4.5,2400]
["PRRA660 RTU-1&2",64.92513277042481,69.925132770424796,76.925132770424796,83.925132770424824,81.925132770424796,82.925132770424796,84.925132770424796,76.925132770424796,90.090584641542051,null,69.925132770424796,75.925132770424796,84.92513277042481,94.925132770424796,96.925132770424796,93.92513277042481,91.925132770424824,84.925132770424796,101.04890209726518,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"450mm",null,null,null,"450mm"]
["PRRA480 RTU-3",59.716962825222538,62.716962825222538,73.716962825222538,72.716962825222538,73.716962825222538,69.716962825222538,69.716962825222538,65.716962825222538,79.592136724173557,null,64.716962825222538,69.716962825222538,82.716962825222538,85.716962825222538,86.716962825222538,81.716962825222538,78.716962825222538,72.716962825222538,91.083717311778003,null,null,null,null,null,null,null,null,"500mm",91,77,79,76,71,69,67,63,92,92,87,83,78,77,72,66,63,94,3835,2,1290,null,"500mm",1290,3835,2,"500mm",91,77,79,76,71,69,67,63,92,92,87,83,78,77,72,66,63,94,3835,2,1290]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"560mm",null,null,null,"560mm"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"630mm",null,null,null,"630mm"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Dual 14\" AF",{"$f":"10*LOG(10^(AD14/10)+10^(AD14/10))","v":91.010299956639841},{"$f":"10*LOG(10^(AE14/10)+10^(AE14/10))","v":83.010299956639813},81.010299956639813,85.010299956639813,78.010299956639827,76.010299956639813,70.010299956639827,67.010299956639827,93.010299956639813,97.010299956639813,89.010299956639813,87.010299956639813,91.010299956639841,84.010299956639813,82.010299956639813,76.010299956639813,73.010299956639813,99.010299956639813,2600,5,2670,4000,"Dual 14\" AF",3074,4884,2.87,"Dual 14\" AF",{"$f":"10*LOG(10^(BE14/10)+10^(BE14/10))","v":91.010299956639841},{"$f":"10*LOG(10^(BF14/10)+10^(BF14/10))","v":83.010299956639813},81.010299956639813,85.010299956639813,78.010299956639827,76.010299956639813,70.010299956639827,67.010299956639827,93.010299956639813,97.010299956639813,89.010299956639813,87.010299956639813,91.010299956639841,84.010299956639813,82.010299956639813,76.010299956639813,73.010299956639813,99.010299956639813,2600,5,2670]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Dual 16\" AF",{"$f":"10*LOG(10^(AD15/10)+10^(AD15/10))","v":90.010299956639813},85.010299956639813,84.010299956639813,87.010299956639813,80.010299956639827,76.010299956639813,71.010299956639813,69.010299956639813,94.010299956639827,88.010299956639813,83.010299956639813,84.010299956639813,90.010299956639813,87.010299956639813,84.010299956639813,80.010299956639827,78.010299956639827,95.010299956639827,2600,5,2520,3700,"Dual 16\" AF",3416,6909,6.16,"Dual 16\" AF",{"$f":"10*LOG(10^(BE15/10)+10^(BE15/10))","v":103.01029995663981},97.010299956639813,93.010299956639813,96.010299956639813,91.010299956639841,90.010299956639813,86.010299956639813,88.010299956639813,105.01029995663983,100.01029995663981,93.010299956639813,93.010299956639813,101.01029995663981,98.010299956639813,96.010299956639813,91.010299956639841,89.010299956639813,106.01029995663984,7500,4.16,3385]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Dual 18\" AF",78.010299956639827,76.010299956639813,80.010299956639827,77.010299956639827,77.010299956639827,73.010299956639813,70.010299956639827,64.010299956639813,86.010299956639813,86.010299956639813,82.010299956639813,90.010299956639813,88.010299956639813,87.010299956639813,82.010299956639813,77.010299956639827,73.010299956639813,94.010299956639827,4379,3.31,1816,3300,"Dual 18\" AF",2582,7909,4.13,"Dual 18\" AF",93.010299956639813,90.010299956639813,91.010299956639841,92.010299956639841,87.010299956639813,85.010299956639813,86.010299956639813,81.010299956639813,98.010299956639813,98.010299956639813,94.010299956639827,97.010299956639813,102.01029995663981,100.01029995663981,96.010299956639813,92.010299956639841,85.010299956639813,106.01029995663984,8500,3,2585]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Dual 20\" AF",80.010299956639827,76.010299956639813,86.010299956639813,74.010299956639813,77.010299956639827,72.010299956639813,70.010299956639827,63.010299956639813,88.010299956639813,86.010299956639813,81.010299956639813,91.010299956639841,87.010299956639813,87.010299956639813,82.010299956639813,79.010299956639813,75.010299956639827,94.010299956639827,5500,3,1624,2850,"Dual 20\" AF",2032,8363,3.17,"Dual 20\" AF",95.010299956639827,90.010299956639813,90.010299956639813,91.010299956639841,86.010299956639813,86.010299956639813,88.010299956639813,82.010299956639813,99.010299956639813,97.010299956639813,93.010299956639813,95.010299956639827,99.010299956639813,98.010299956639813,94.010299956639827,92.010299956639841,87.010299956639813,105.01029995663983,10000,3,2278]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hz",63,125,250,500,1000,2000,4000,8000,"Tot.",63,125,250,500,1000,2000,4000,8000,"Tot."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP($C$7,$AC$4:$AT$33,AC2,FALSE)","v":"25\" AF"},{"$f":"IF($AD$39=TRUE,-3+IF($BA$2=0,VLOOKUP($J$7,AREA1,AD2,FALSE)+50*(LOG($L$9/(VLOOKUP($J$7,AREA1,22,FALSE)))),VLOOKUP($J$7,AREA2,BE2,FALSE)+50*(LOG($L$9/(VLOOKUP($J$7,AREA2,22,FALSE))))),-6+IF($BA$1=0,VLOOKUP($C$7,AREA1,AD2,FALSE)+50*(LOG($E$9/(VLOOKUP($C$7,AREA1,22,FALSE)))),VLOOKUP($C$7,AREA2,BE2,FALSE)+50*(LOG($E$9/(VLOOKUP($C$7,AREA2,22,FALSE))))))","v":85.716962825222538},78.716962825222538,82.716962825222538,75.716962825222538,73.716962825222538,68.716962825222538,68.716962825222538,66.716962825222538,88.716962825222538,{"$f":"-3+IF($BA$1=0,VLOOKUP($C$7,AREA1,AM2,FALSE)+50*(LOG($AD$38/(VLOOKUP($C$7,AREA1,22,FALSE)))),VLOOKUP($C$7,AREA2,BN2,FALSE)+50*(LOG($AD$38/(VLOOKUP($C$7,AREA2,22,FALSE)))))","v":90.716962825222538},85.716962825222538,91.716962825222538,88.716962825222538,86.716962825222538,80.716962825222538,77.716962825222538,73.716962825222538,{"$f":"IF($BA$1=0,VLOOKUP($C$7,AREA1,AU2,FALSE)+50*(LOG($AD$38/(VLOOKUP($C$7,AREA1,22,FALSE)))),VLOOKUP($C$7,AREA2,BV2,FALSE)+50*(LOG($AD$38/(VLOOKUP($C$7,AREA2,22,FALSE)))))","v":99.716962825222538}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"CFM",{"$f":"E7","v":12440}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"TSP",{"$f":"E8","v":3.4}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"RPM",{"$f":"E9","v":1573}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Exhaust",false,{"$f":"IF(AD39=TRUE,0,0)","v":0}]

{"sheet":"Sheet3","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}