716.551.7900   info@ndustria.com   www.ndustria.com

High Intensity, Gas-Fired, Infrared Heaters

NDUSTRIA™ GG-SERIES

WRITTEN SPECIFICATIONS

Gas-fired infrared space heaters shall be furnished and installed in accordance with governing codes and as shown per building drawing(s) as described below:

- High Intensity Infrared Heater Specifications

  - High intensity infrared heaters shall be NDUSTRIA™ GG series ceramic heaters, model number GG_________, rated at _____________ Btu/hr, as manufactured by NDUSTRIA. Heaters shall be equipped with a 24-volt direct spark ignition system with 100% gas shutoff.

  - High intensity infrared heaters shall be designed certified by CSA.

  - The manufacturer shall provide a written limited warranty of five (5) years covering the emitter tiles and a limited warranty of one (1) year for all components utilized in the heater's control assembly.

  - High Intensity Infrared Heaters shall be designed to operate when burning natural gas having a heat value of 1025 BTU per cubic foot with a specific gravity of 0.62, or when burning propane gas having a heat value of 2500 BTU per cubic foot with a specific gravity of 1.53.

  - The ceramic burner face shall operate at a temperature range of 1660 degrees F to 1810 degrees F and shall incorporate a secondary re-radiating surface of stainless steel rods to obtain optimum operating temperature and radiant output.

- High Intensity Infrared Burner Controls

  - Heaters shall be equipped with the following control system

    - Direct Spark Ignition System with direct spark ignition of the main burner through a solid state ignition module operating a spark electrode. Loss of power causes 100% safety shut-off of main burner(s). System operates on 120 or 24 volts (NFS-2 or PFS-2).

- High Intensity Infrared Heater Construction

  - Heaters shall be made of aluminized steel body construction and shall consist of multiple burner heads. Heaters shall utilize special honeycomb tile design for increased radiant output.

  - Heaters shall operate satisfactorily in any position from horizontal to thirty-five (35º) degrees from horizontal.  Heaters shall be design certified by C.S.A. to American National Standard Z83.19-latest edition/CSA Standard 2.35-latest edition.

  - The heater reflector housing shall be constructed of one-side bright polished aluminum. The emitter shall be composed of a perforated ceramic tile on which combustion takes place on the surface. The burner plenum shall be constructed of aluminized steel of one-piece drawn construction. The heater shall be of a modular design employing multiple burners to achieve the specified input.

  - The venturi is constructed of stainless or aluminized steel.

  - The secondary re-radiating rods shall be constructed of high temperature stainless steel alloy placed in close proximity of the ceramic burner face.

- Typical Wiring Diagrams

  - (Reference image on GG spec)

  - Note: Local codes may require that an exhauster is interlocked with the thermostat. Thermostat Hot Neutral Exhaust Fan GG Series Heater Transformer (required on 24V heaters) GG Series Heater GG Series